## Sheet1
| Name Field | Alarm - Value - Range | Measured | Type of Value | Length | Stored value format as max value | Sign | Notes
Significant digits, number of values after decimal point
v | Timestamp |  |  | Time Value |  |  | NA
v | Engine Oil Pressure | Alarms at 1.5 bar min & 7 bar max | Pressure | Decimal | 3, 1 | 99.9 | Pos
v | Engine Oil Temperature | Alarm at 130°C max | Temperature | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Engine RPM
v | Primary Coolant Pressure | Alarm at 2 bar max | Pressure | Decimal | 3, 1 | 99.9 | Pos
| Primary Coolant Header Tank Level | ? Value Range ?
v | Primary Coolant Temperature | Alarm at 100°C, shutdown at 110°C. | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Secondary Coolant Pressure | Alarm at 3 bar max | Pressure | Decimal | 3, 1 | 99.9 | Pos
v | Secondary Coolant Post Site Heat Exchanger | Delta T 85°C max (changeover parameter for dump cooling) | Temperature,measuring delta of 10°C | Decimal | 3, 1 | 99.9 | Pos & Neg
v | Secondary Coolant Pre Exhaust Gas Heat Exchanger Temperature | Delta T | Temperature,measuring delta of approx. 6°C | Decimal | 3, 1 | 99.9 | Pos & Neg
v | Secondary Coolant Post Exhaust Gas Heat Exchanger Temperature | Delta T | Temperature,measuring delta of approx. 6°C | Decimal | 3, 1 | 99.9 | Pos & Neg
v | Temperature Acoustic Chamber – Enclosure 1 #1 | Alarm 100°C max | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Temperature Acoustic Chamber – Enclosure 1 #2 | Alarm 100°C max | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Temperature Acoustic Chamber – Enclosure 2 | Alarm 100°C max | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Starting Fuel Level | Alarm when low at approx. 50L. Tank max 500L | Fuel level | Decimal | 4, 1 | 999.9 | Pos
v | Main Fuel Tank Level | Alarm when low approx. 1500L. Tank max 50,000L | Fuel Level | Decimal | 6, 1 | 99999.9 | Pos
v | Main Fuel Pressure Pre Filter | Alarm (1 bar Delta P) | Pressure | Decimal | 3, 1 | 99.9 | Pos
v | Main Fuel Pressure Post Filter | Alarm (1 bar Delta P) | Pressure | Decimal | 3, 1 | 99.9 | Pos
| Main Fuel Pre Manifold Temperature | Alarm (Glycerine 95-100°C) | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Fuel Temperature Pre Fuel Heater | Alarm (Delta T Low Warning at 75°C) | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Fuel Temperature Post Fuel Heater | Alarm (Delta T Low Warning at 75°C) | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
| Bund Level 1 | Alarm – any fluid level? Value Range ?
| Bund Level 2 | Alarm – any fluid level? Value Range ?
| Bund Level 3 | Alarm – any fluid level? Value Range ?
v | Inlet Air Pre After Cooler Left | Set operational temps 80-100°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Inlet Air Pre After Cooler Right | Set operational temps 80-100°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Inlet Air Temperature Pre Turbocharger Left | 10-40°C | Temperature | Decimal | 3, 1 | 99.9 | Pos & Neg
v | Inlet Air Temperature Pre Turbocharger Right | 10-40°C | Temperature | Decimal | 3, 1 | 99.9 | Pos & Neg
v | Inlet Air Temperature Pre After Cooler Left | 80-120°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Inlet Air Temperature Pre After Cooler Right | 80-120°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Inlet Air Pressure Manifold Left | 0-2 bar | Pressure | Decimal | 5, 4 | 9.9999 | Pos
v | Inlet Air Pressure Manifold Right | 0-2 bar | Pressure | Decimal | 5, 4 | 9.9999 | Pos
| Water Temperature Pre After Cooler | 75-115°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
| Water Temperature Post After Cooler | 75-115°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
| Exhaust Back Pressure Left | 50-100 millibars (0-0.5 bar level) | Pressure | Decimal | 4, 3 | 9.999 | Pos
| Exhaust Back Pressure Right | 50-100 millibars (0-0.5 bar level) | Pressure | Decimal | 4, 3 | 9.999 | Pos
v | Exhaust Temperature Pre Turbocharger Left | 0-600°C, alarm at 620°C, shutdown at 650°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Exhaust Temperature Post Turbocharger Left | 0-550°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Exhaust Temperature Pre Turbocharger Right | 0-600°C, alarm at 620°C, shutdown at 650°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Exhaust Temperature Post Turbocharger Right | 0-550°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
v | Pre SCR Temperature | 0-550°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
| Exhaust Temperature Post Heat Exchanger | 0-200°C | Temperature | Decimal | 4, 1 | 999.9 | Pos & Neg
| NOx Sensor (Option) | ? Value Range ?
v | Mains Voltage – Phase 1 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Mains Voltage – Phase 2 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Mains Voltage – Phase 3 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Mains Frequency | 0-100 | Frequency | Decimal | 4, 1 | 999.9 | Pos
v | Generator Voltage – Phase 1 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Generator Voltage – Phase 2 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Generator Voltage – Phase 3 | 0-1000 | Voltage | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Generator Frequency | 0-100 | Frequency | Decimal | 4, 1 | 999.9 | Pos
v | Generator Power Factor – Phase 1 | Range 0 – 1 | cos phi | Decimal | 3, 2 | 9.99 | Pos & Neg
v | Generator Power Factor – Phase 2 | Range 0 – 1 | cos phi | Decimal | 3, 2 | 9.99 | Pos & Neg
v | Generator Power Factor – Phase 3 | Range 0 – 1 | cos phi | Decimal | 3, 2 | 9.99 | Pos & Neg
v | Generator Amperage – Phase 1 | 0-1000 | Ampere | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Generator Amperage – Phase 2 | 0-1000 | Ampere | Decimal | 5, 1 | 9999.9 | Pos & Neg
v | Generator Amperage – Phase 3 | 0-1000 | Ampere | Decimal | 5, 1 | 9999.9 | Pos & Neg
| Electrical Output on Start/Non-Renewable Fuel |  | KWh – Electrical (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Electrical Output on Running/Renewable Fuel |  | KWh – Electrical (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Total energy |  | KWh – Electrical (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Parasitic Load |  | KWh – Electrical (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Ofgem Claimable Energy – Non Parasitic Load (Total Energy – Parasitic Load) |  | KWh – Electrical (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
v | Site Flow Temperature |  | Temperature | Decimal | 4, 1 | 999.9 | Pos
v | Site Return Temperature |  | Temperature | Decimal | 4, 1 | 999.9 | Pos
v | Site Flow Rate | ? Value Range ? | Flow Rate
| Fuel 1 – Non-Renewable – kWh Thermal |  | KWh – Thermal (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Fuel 2 – Renewable – kWh Thermal |  | KWh – Thermal (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Fuel 3 – Renewable – kWh Thermal |  | KWh – Thermal (Max value 1000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
| Renewable Energy Total (Non Parasitic Electrical (kWh) plus Thermal (kWh)) |  | KWh – Thermal (Max value 2000 Gwh) | Decimal | 12, 2 | 9999999999.99 | Pos
Note on B9: This will not be on the data, it will be an alarm on the control screen. It is a single value low level warning. If the alarm goes off then emails will be sent out and the problem addressed.
Note on B25: This will not be on the data, only an alarm on the control screen. It is a single value low level warning. If the alarm goes off then emails will be sent out and the problem addressed.
Note on B34: These two are still on the list, just above "Exhaust Temperature Pre Turbo Left".
Note on B36: These were an option that could be included in the .csv data file and can be recorded if you would like them to be. It is not something that is critical but after talking to John McNeil (who you spoke to on the phone to recently) it might be worth putting them in if you would like to record their data.
Note on B38: This will now be only one sensor (as its where the 2 exhausts join into 1, so only 1 sensor required). So from now on it will be "Exhaust Back Pressure". Similar to the above, this was also an option on the data logs, which after talking to John would probably be worth putting into the data logs.
Note on B45: Similar to the 2 comments above, this was also an option, not critical data but after recent discussions it would be good to add it in.
Note on B46: It's still not 100% yet if this will be included or not. If it's possible for you to leave it out and include it at a later date I would advise that.
Note on B61: These can be added if required but are not required to be recorded every cycle and have not been recorded on the data logs of past projects. The reason for this is normally only a single monthly balance/reading is required on each one so it is best to record these readings once a month.
Note on B69: These are calcualtions done afterwards based on the information from the above. Therefore will not be recorded on the data log but can be calculated from the above monthly readings.